## Load Calc Sheet
Load Section | Entries | Descriptions
1. General Lighting Load |  | Enter square footage of building (does not include porches or other non future habitable areas)
| 0 | VA
2. Small Appliance Load |  | Enter number of 20 amp branch circuts (minimum 2)
| 0 | VA
3. Laundry Branch Circuit Load |  | Enter number of Laundry 20 amp branch circuts (minimum 1)
| 0 | VA
4. Total General Lighting, Small Appliance, Laundry Loads | 0 | VA
5. Net computed General Lighting, Small Appliance, Laundry Loads | 1950 | VA
6. Electric Range, Wall Mount Ovens, Counter Top Cook Units (NEC Table 220.55 |  | Enter number of Devices
| 0 | VA
7. Electric Dryer |  | Enter Nameplate Rating of Electric Dryer in VA
| 0 | VA
8. Electric Furnace, Air Conditioner, Heat Pump |  | Enter VA for Each Appliance
0
9. Net Computed General Lighting, Small Appliance, Laundry, Ranges, Ovens, Cooktop Units, HVAC Loads | 1950
10. Fastened in Place Appliances (Appliances in addition to Electric Ranges, electric Cloths Dryers, Electric Space Heating and AC Equipment) |  | Water Heater
Dishwater
Microwave
Garage Door Opener
2nd Garage Door Opener
Food Waste Disposal
Water Pump
Gas Fred Furnace
Sump Pump
Other
Other
Other
Other
Other
0
11. Demand Factor for Fastened in Place Appliances (75% for four or more, 100% for less than 4) | 0
12. Total Computed Load | 1950
13. Motor End Rush Load |  | Add Largest Motor VA
0
14. Grand Total Computed Loads and Motor End Rush | 1950
15. Continous Duty Appliances |  | Hot Tubs
EV Chargers
Other
Other
Other
0
16. Minimum Ampacity for Underground Service Entrance Conductors | 8.125
Site Altitude
Generator Brand
Air or Liquid Cooled
Phase
MCB Size

## NEC Tables
220.55 Demand Factors and Loads for electrci Ranges, Wall Mounted Ovens, Cook Tops, and other household cooking appliances over 1 3/4 kW (1750W).
Number of Applinaces | Column A | Column B | Column C | Each additional Range
1 | 80 | 80 | 8
2 | 75 | 65 | 11
3 | 70 | 55 | 14
4 | 66 | 50 | 17
5 | 62 | 45 | 20
6 | 59 | 43 | 21
7 | 56 | 40 | 22
8 | 53 | 36 | 23
9 | 51 | 35 | 24
10 | 49 | 34 | 25
11 | 47 | 32 | 26
12 | 45 | 32 | 27
13 | 43 | 32 | 28
14 | 41 | 32 | 29
15 | 40 | 32 | 30
16 | 39 | 32 | 31
17 | 38 | 32 | 32
18 | 37 | 32 | 33
19 | 36 | 32 | 34
20 | 35 | 32 | 35
21 | 34 | 32 | 36
22 | 33 | 32 | 37
23 | 32 | 32 | 38
24 | 31 | 32 | 39
25 | 30 | 32 | 40
26 | 30 | 32 | 15 | 1
27 | 30 | 32 | 15 | 1
28 | 30 | 32 | 15 | 1
29 | 30 | 32 | 15 | 1
30 | 30 | 32 | 15 | 1
31 | 30 | 32 | 15 | 1
32 | 30 | 32 | 15 | 1
33 | 30 | 32 | 15 | 1
34 | 30 | 32 | 15 | 1
35 | 30 | 32 | 15 | 1
36 | 30 | 32 | 15 | 1
37 | 30 | 32 | 15 | 1
38 | 30 | 32 | 15 | 1
39 | 30 | 32 | 15 | 1
40 | 30 | 32 | 15 | 1
41 | 30 | 32 | 25 | 0.75
42 | 30 | 32 | 25 | 0.75
43 | 30 | 32 | 25 | 0.75
44 | 30 | 32 | 25 | 0.75
45 | 30 | 32 | 25 | 0.75
46 | 30 | 32 | 25 | 0.75
47 | 30 | 32 | 25 | 0.75
48 | 30 | 32 | 25 | 0.75
49 | 30 | 32 | 25 | 0.75
50 | 30 | 32 | 25 | 0.75
51 | 30 | 32 | 25 | 0.75
52 | 30 | 32 | 25 | 0.75
53 | 30 | 32 | 25 | 0.75
54 | 30 | 32 | 25 | 0.75
55 | 30 | 32 | 25 | 0.75
56 | 30 | 32 | 25 | 0.75
57 | 30 | 32 | 25 | 0.75
58 | 30 | 32 | 25 | 0.75
59 | 30 | 32 | 25 | 0.75
60 | 30 | 32 | 25 | 0.75
61 | 30 | 32 | 25 | 0.75